## Version Control
Change information registration form
Version | Reason for change | Change people | Auditor People | Updated Timme
V1.01 |  | 马光源 |  | 2022.01.28
V1.02 | Add air conditioning and fire protection | 魏亚京 |  | 2022.03.14
V1.03 | Adjust the definition name and standardize the protocol format as required | 周文飞 |  | 2022.03.14
V1.03 | Change the number of air conditioners and fire fighters. Note Applicable system | 周文飞 |  | 2022.03.16
V1.06 | Update the Input register for max charge discharge & additional hold registers (all updated contents are marked gray) | 周文飞 |  | 2022.08.04
V1.07 | add pcs ac data | 魏亚京 |  | 2022.08.05
V1.08 | 1. 修改PCS系统工作模式（本地/远程/自动） 2. 增加BMS使能控制，方便VR模式维护 | 魏亚京 |  | 2022.11.05
V1.08.1 | 调整消防和空调地址，修改光伏模块数量 | 魏亚京 |  | 2022.12.03
V1.09 | 增加EOD预警 | 魏亚京 |  | 2023.03.07
V1.10 | 修改总直流功率分辨率 | 魏亚京 |  | 2023.05.05
V1.12 | 增加光伏模块到6个 | 魏亚京 |  | 2023.10.24

## Input Register(FUN CODE 04)
Address (DEC) | Address (HEX) | Meaning | Data Type | Data Accuracy | Remarks | PCMZ50 | PCS Series | solar storage system | GRES system
256 | 100 | Grid Phase Voltage A | uint16 | 0.1V |  | √ | √ | √ | √
257 | 101 | Grid Phase Voltage B | uint16 | 0.1V |  | √ | √ | √ | √
258 | 102 | Grid Phase Voltage C | uint16 | 0.1V |  | √ | √ | √ | √
259 | 103 | Grid Line Voltage AB | uint16 | 0.1V |  | √ | √ | √ | √
260 | 104 | Grid Line Voltage BC | uint16 | 0.1V |  | √ | √ | √ | √
261 | 105 | Grid Line Voltage CA | uint16 | 0.1V |  | √ | √ | √ | √
262 | 106 | Grid Current A | int16 | 0.1A |  | √ | √ | √ | √
263 | 107 | Grid Current B | int16 | 0.1A |  | √ | √ | √ | √
264 | 108 | Grid Current C | int16 | 0.1A |  | √ | √ | √ | √
265 | 109 | Grid Active Power A | int16 | 0.1kW |  | √ | √ | √ | √
266 | 10A | Grid Active Power B | int16 | 0.1kW |  | √ | √ | √ | √
267 | 10B | Grid Active Power C | int16 | 0.1kW |  | √ | √ | √ | √
268 | 10C | Grid Apparent Power A | int16 | 0.1kVA |  | √ | √ | √ | √
269 | 10D | Grid Apparent Power B | int16 | 0.1kVA |  | √ | √ | √ | √
270 | 10E | Grid Apparent Power C | int16 | 0.1kVA |  | √ | √ | √ | √
271 | 10F | Grid Frequency | uint16 | 0.01Hz |  | √ | √ | √ | √
272 | 110 | Number Of Online Modules | uint16 |  |  | √ | √ | √ | √
273 | 111 | Grid Reactive Power A | int16 | 0.1kVar | Run - Grid information module added to the module | √ | √ | √ | √
274 | 112 | Grid Reactive Power B | int16 | 0.1kVar |  | √ | √ | √ | √
275 | 113 | Grid Reactive Power C | int16 | 0.1kVar |  | √ | √ | √ | √
276 | 114 | Grid Power Factor A | int16 | 0.01 |  | √ | √ | √ | √
277 | 115 | Grid Power Factor B | int16 | 0.01 |  | √ | √ | √ | √
278 | 116 | Grid Power Factor C | int16 | 0.01 |  | √ | √ | √ | √
279 | 117 | Total Active Power | int16 | 0.1kW |  | √ | √ | √ | √
280 | 118 | Total Reactive Power | int16 | 0.1kVar |  | √ | √ | √ | √
281 | 119 | Total Apparent Power | uint16 | 0.1kVA |  | √ | √ | √ | √
282 | 11A | Total DC power | int16 | 0.1kW | Points of power - DC information | √ | √ | √ | √
283 | 11B | Total DC Charge Energy (high bytes) | uint32 | kWh |  | × | √ | √ | √
284 | 11C | Total DC Charge Energy (low bytes) |  |  |  | × | √ | √ | √
285 | 11D | Total DC Discharge Energy (high bytes) | uint32 | kWh |  | × | √ | √ | √
286 | 11E | Total DC Discharge Energy (low bytes) |  |  |  | × | √ | √ | √
287 | 11F | Total AC Charge Energy (high bytes) | uint32 | kWh |  | × | √ | √ | √
288 | 120 | Total AC Charge Energy (low bytes) |  |  |  | × | √ | √ | √
289 | 121 | Total AC Discharge Energy(high bytes) | uint32 | kWh |  | × | √ | √ | √
290 | 122 | Total AC Discharge Energy (low bytes) |  |  |  | × | √ | √ | √
291 | 123 | Total Reactive Power Energy (high bytes) | uint32 | kWh |  | × | √ | √ | √
292 | 124 | Total Reactive Power Energy (low bytes) |  |  |  | × | √ | √ | √
293 | 125 | Load Line Voltage AB | uint16 | 0.1V |  | √ | √ | √ | √
294 | 126 | Load Line Voltage BC | uint16 | 0.1V |  | √ | √ | √ | √
295 | 127 | Load Line Voltage AC | uint16 | 0.1V |  | √ | √ | √ | √
296 | 128 | Load Current A | uint16 | 0.1A |  | √ | √ | √ | √
297 | 129 | Load Current B | uint16 | 0.1A |  | √ | √ | √ | √
298 | 12A | Load Current C | uint16 | 0.1A |  | √ | √ | √ | √
299 | 12B | Load Active Power A | uint16 | 0.1kW |  | √ | √ | √ | √
300 | 12C | Load Active Power B | uint16 | 0.1kW |  | √ | √ | √ | √
301 | 12D | Load Active Power C | uint16 | 0.1kW |  | √ | √ | √ | √
302 | 12E | Load Apparent Power A | uint16 | 0.1kVA |  | √ | √ | √ | √
303 | 12F | Load Apparent Power B | uint16 | 0.1kVA |  | √ | √ | √ | √
304 | 130 | Load Apparent Power C | uint16 | 0.1kVA |  | √ | √ | √ | √
305 | 131 | Total Load Active Power | uint16 | 0.1kW
306 | 132 | Total Load Apparent Power | uint16 | 0.1kVA
307 | 133 | Output Frequency | uint16 | 0.01HZ
308 | 134 | PCS Active Power A | uint16 | 0.1kW
309 | 135 | PCS Active Power B | uint16 | 0.1kW
310 | 136 | PCS Active Power C | uint16 | 0.1kW
311 | 137 | PCS Reactive Power A | uint16 | 0.1kVar
312 | 138 | PCS Reactive Power B | uint16 | 0.1kVar
313 | 139 | PCS Reactive Power C | uint16 | 0.1kVar
314 | 13A | PCS Apparent Power A | uint16 | 0.1kVA
315 | 13B | PCS Apparent Power B | uint16 | 0.1kVA
316 | 13C | PCS Apparent Power C | uint16 | 0.1kVA
317 | 13D | Total PCS Active Power | uint16 | 0.1kW
318 | 13E | Total PCS Reactive Power | uint16 | 0.1kVar
319 | 13F | Total PCS Apparent Power | uint16 | 0.1kVA
Address (decimal) | Address (hexadecimal) | Meaning | Data Type | Data Accuracy | Note: Battery analog quantity
512 | 200+(N-1)*10 | #1 DC Voltage | uint16 | 0.1V | Note: N Maximum: 0x0A | √ | √ | √ | √
513 | 201+(N-1)*10 | #1DC Current | int16 | 0.1A |  | √ | √ | √ | √
514 | 202+(N-1)*10 | #1DC Power | int16 | 0.01kW |  | √ | √ | √ | √
515 | 203+(N-1)*10 | Battery#1 SOC | uint16 |  |  | √ | √ | √ | √
516 | 204+(N-1)*10 | Battery#1 SOH | uint16 |  |  | √ | √ | √ | √
517 | 205+(N-1)*10 | Max rechargeable current | uint16 | 0.1A
518 | 206+(N-1)*10 | Max dischargeable current | uint16 | 0.1A
519 | 207+(N-1)*10 | Max allowable charging voltage | uint16 | 0.1V
520 | 208+(N-1)*10 | Max allowable discharging voltage | uint16 | 0.1V
521 | 209+(N-1)*10 | #1BMS Alarm | uint16 |  | Note- 7: BMS Alarm
522 | 20A+(N-1)*10 | #1BMS State | uint16 |  | Note- 8: BMS State
523 | 20B+(N-1)*10 | Battery#1 Alarm Bit48-63 | unit64 |  | Table 4
524 | 20C+(N-1)*10 | Battery#1 Alarm Bit32-47
525 | 20D+(N-1)*10 | Battery#1 Alarm Bit16-31
526 | 20E+(N-1)*10 | Battery#1 Alarm Bit0-15
… …
656 | 200+(N-1)*10 | #N DC Voltage | uint16 | 0.1V
657 | 201+(N-1)*10 | #N DC Current | int16 | 0.1A
658 | 202+(N-1)*10 | #N DC Power | int16 | 0.01kW
659 | 203+(N-1)*10 | Battery#1 SOC | uint16
660 | 204+(N-1)*10 | Battery#1 SOH | uint16
661 | 205+(N-1)*10 | Max rechargeable current | uint16 | 0.1A
662 | 206+(N-1)*10 | Max dischargeable current | uint16 | 0.1A
663 | 207+(N-1)*10 | Max allowable charging voltage | uint16 | 0.1V
664 | 208+(N-1)*10 | Max allowable discharging voltage | uint16 | 0.1V
665 | 209+(N-1)*10 | #N BMS Alarm | uint16 |  | Note- 7: BMS Alarm
666 | 20A+(N-1)*10 | #N BMS State | uint16 |  | Note- 8: BMS State
667 | 20B+(N-1)*10 | Battery#N Alarm Bit48-63 | unit64 |  | Table 4
668 | 20C+(N-1)*10 | Battery#N Alarm Bit32-47
669 | 20D+(N-1)*10 | Battery#N Alarm Bit16-31
670 | 20E+(N-1)*10 | Battery#N Alarm Bit0-15
Address (decimal) | Address (hexadecimal) | Meaning | Data Type | Data Accuracy | Remarks
1024 | 400+(N-1)*10 | P.#1 module temperature | uint16 |  | 备注：N Max：0x10
1025 | 401+(N-1)*10 | P.#1 state1 |  |  | Table 2
1026 | 402+(N-1)*10 | P.#1 state2
1027 | 403+(N-1)*10 | P.#1 state3
1028 | 404+(N-1)*10 | P.#1 alarm1 |  |  | Table 3
1029 | 405+(N-1)*10 | P.#1 alarm2
1030 | 406+(N-1)*10 | P.#1 alarm3
… …
1264 | 400+(N-1)*10 | P.#16 module temperature | uint16
1265 | 401+(N-1)*10 | P.#16 state1 |  |  | Table 2
1266 | 402+(N-1)*10 | P.#16 state2
1267 | 403+(N-1)*10 | P.#16 state3
1268 | 404+(N-1)*10 | P.#16 alarm1 |  |  | Table 3
1269 | 405+(N-1)*10 | P.#16 alarm2
1270 | 406+(N-1)*10 | P.#16 alarm3
Address (decimal) | Address (hexadecimal) | Meaning | Data Type | Data Accuracy | Remarks
1280 | 500 | System State | uint16 |  | Note 1: PCS system status | √ | √ | √ | √
1281 | 501 | Grid State | uint16 |  | Note 2: Status on the AC side | √ | √ | √ | √
1282 | 502 | P.#1 DCState | uint16 |  | Note 3: Dc status | √ | √ | √ | √
1283 | 503 | P.#2 DCState | uint16 |  |  | √ | √ | √ | √
1284 | 504 | P.#3 DCState | uint16 |  |  | √ | √ | √ | √
1285 | 505 | P.#4 DCState | uint16 |  |  | √ | √ | √ | √
1286 | 506 | P.#5 DCState | uint16 |  |  | √ | √ | √ | √
1287 | 507 | P.#6 DCState | uint16 |  |  | √ | √ | √ | √
1288 | 508 | P.#7 DCState | uint16 |  |  | √ | √ | √ | √
1289 | 509 | P.#8 DCState | uint16 |  |  | √ | √ | √ | √
1290 | 50A | P.#9 DCState | uint16 |  |  | √ | √ | √ | √
1291 | 50B | P.#10 DCState | uint16 |  |  | √ | √ | √ | √
1292 | 50C | M.#1 State | uint16 |  | Note 4: MPPT status | × | × | √ | √
1293 | 50D | M.#2 State | uint16 |  |  | × | × | √ | √
1294 | 50E | M.#3 State | uint16 |  |  | × | × | √ | √
1295 | 50F | System alarm bits | uint16 |  | Note 9:system alarm
Address (decimal) | Address (hexadecimal) | Meaning | Data Type | Data Accuracy | Remarks: amount of photovoltaic simulation
1536 | 600 | PV cumulative energy(high bytes) | uint32 | kWh
1537 | 601 | PV umulative energy(low bytes)
1538 | 602+(N-1)*20 | M.#1 PV Volt 1 | uint16 | 0.1V | Note: N Maximum: 0x06 | × | × | √ | √
1539 | 603+(N-1)*20 | M.#1 PV Volt 2 | uint16 | 0.1V |  | × | × | √ | √
1540 | 604+(N-1)*20 | M.#1 PV Volt 3 | uint16 | 0.1V |  | × | × | √ | √
1541 | 605+(N-1)*20 | M.#1 PV Current 1 | uint16 | 0.1A |  | × | × | √ | √
1542 | 606+(N-1)*20 | M.#1 PV Current 2 | uint16 | 0.1A |  | × | × | √ | √
1543 | 607+(N-1)*20 | M.#1 PV Current 3 | uint16 | 0.1A |  | × | × | √ | √
1544 | 608+(N-1)*20 | M.#1 PV Power 1 | uint16 | 0.1kW |  | × | × | √ | √
1545 | 609+(N-1)*20 | M.#1 PV Power 2 | uint16 | 0.1kW |  | × | × | √ | √
1546 | 60A+(N-1)*20 | M.#1 PV Power 3 | uint16 | 0.1kW |  | × | × | √ | √
1547 | 60B+(N-1)*20 | M.#1 OutputPower | uint16 | 0.1kW |  | × | × | √ | √
… …
1602 | 602+(N-1)*20 | M.#N PV Volt 1 | uint16 | 0.1V |  | × | × | √ | √
1603 | 603+(N-1)*20 | M.#N PV Volt 2 | uint16 | 0.1V |  | × | × | √ | √
1604 | 604+(N-1)*20 | M.#N PV Volt 3 | uint16 | 0.1V |  | × | × | √ | √
1605 | 605+(N-1)*20 | M.#N PV Current 1 | uint16 | 0.1A |  | × | × | √ | √
1606 | 606+(N-1)*20 | M.#N PV Current 2 | uint16 | 0.1A |  | × | × | √ | √
1607 | 607+(N-1)*20 | M.#N PV Current 3 | uint16 | 0.1A |  | × | × | √ | √
1608 | 608+(N-1)*20 | M.#N PV Power 1 | uint16 | 0.1kW |  | × | × | √ | √
1609 | 609+(N-1)*20 | M.#N PV Power 2 | uint16 | 0.1kW |  | × | × | √ | √
1610 | 60A+(N-1)*20 | M.#N PV Power 3 | uint16 | 0.1kW |  | × | × | √ | √
1611 | 60B+(N-1)*20 | M.#N OutputPower | uint16 | 0.1kW |  | × | × | √ | √
Address (decimal) | Address (hexadecimal) | Meaning | Data Type | Data Accuracy | Remarks: air conditioning and fire protection
1792 | 700+(N-1)*2 | #1 Ambient Temperature | uint16 | 0.1℃ | Note: N Maximum: A | × | × | × | √
1793 | 701+(N-1)*2 | #1 Air Condition State | uint16 |  | Note 5: (Air Conditioner state) | × | × | × | √
| … … |  |  |  |  | × | × | × | √
1810 | 700+(N-1)*2 | #N Ambient Temperature | uint16 | 0.1℃ |  | × | × | × | √
1811 | 701+(N-1)*2 | #N Air Condition State | uint16 |  |  | × | × | × | √
1812 | 714 | Fire Fighting State | uint16 |  | Note 6:(Fire Fighting State) maximum: 3 | × | × | × | √
The following is set to 1 to indicate that the alarm or fault has occurred
Display Register Value Bit | bit0 | bit1 | bit2 | bit3 | bit4 | bit5 | bit6 | bit7 | bit8 | bit9 | bit10 | bit11 | bit12 | bit13 | bit14 | bit15
Note 1: PCS State | Emergency Stop 0：None 1：Stop | SPD State 0: Normal 1: Fault | 0:System-Off 1:System-On | Working state: 0: None Supply; 1: Off-Grid Supply; 2: PQ On-Grid Supply; 3: VR On-Grid Supply; 4: Grid Supply |  |  |  | Transformer Over Temperature | Transformer Over Temperature Protection | 1: Normal Shutdown 2: Fault Shutdown 3: Normal Operation 4: Alarm Operation 5: Starting |  |  | 0:Manual 1:Auto 2:Remote |  | Fault Self-locking | Derated Operation
Note 2: Grid State | bit0: Voltage Abnormal; bit1: Frequency Abnormal; bit2: Phase Sequence Abnormal
Note 3: DC State | bit0: DC Under Voltage; bit1: DC Over Voltage; bit2: Reversed; bit3: Disconnected; bit4: BMS Communication Abnormal
Note 4: MPPT state | bit0: Input State 0 Normal; 1 Under-voltage; 2 Over-voltag; 3 Reversed; 4 Disconnected；; bit3: Input current limit status; bit4: Output current limit status; bit5: Output voltage limiting status; bit6: Emergency Stop 0：None 1：Stop; bit7: 0:System-Off 1:System-On; bit8: module is overtemperature; bit9: PV module is powered off due to Internal Faults; bit10: Fan Fault
Note 5: AC State | bit0: 0: OFF 1: ON; bit1: High-low Pressure 0: Normal 1: Alarm; bit2: Sensor 0: Normal 1: Fault; bit3: Compressor 0: Normal 1: Fault; bit4: High-low Volt 0:Normal 1: Alarm; bit5: High-low Temperature 0: Normal 1:Alarm
Note 6: Fire Fighting State | bit0: #1 Fire Fighting 0: Normal 1: Alarm; bit1: #2 Fire Fighting 0: Normal 1: Alarm; bit2: #3 Fire Fighting 0: Normal 1: Alarm
Note 7: BMS Alarm | BMU communication is interrupted | EPO shutdown | Discharge contactor fault shutdown | Charge contactor fault shutdown | Total voltage abnormal shutdown | Abnormal cell voltage shutdown | Charge overcurrent protection shutdown | Discharge overcurrent protection shutdown | Low temperature protection shutdown | Over temperature protection shutdown
Note 8: BMS State | 0: Power On, 1 Start, 2 Stand, 3 Charge, 4 Discharge, 5 Charge wait, 6 Discharge Wait, 7 Lock |  |  | 1: Discharge Prohibited | 1: Charging Prohibited | Over Temperature Warning | Low Temperature Warning | Total Over-voltage Warning | Total Under-voltage Warning | Parallel Communication Exception | Parallel Address Conflict | EqualizatIon Failed | Circuit Breaker Open
Note 9: system Alarm | bit0: EOD alarm 0: normal 1: alarm
The upper computer processing:
1. input register DC information, address is not continuous, only support security group query;
2.The lower computer does not store the data of the upper computer's register Settings. The upper computer needs to deliver Settings before starting up each time (working mode, AC side voltage and frequency Settings can be started up, and other Settings can be set according to customer requirements).
3.Hold registers only support read/write but write only support single register.
Table 2：detailed list of state information
Data words | bit0: bit; bit1: state name; bit2: meaning
u16Word1All | bit0: BIT0; bit1: DC side status; bit2: =0 normal；=1 Undervoltage(540)；=2 Overvoltage(541)； =3 Positive and negative reversed(536)；=4 Not connected(535)；
BIT1
BIT2
| BIT3 | The current mode of operation | =0 Illegal mode；=1Inverter mode； =2 PQ discharge mode；=3 Charger mode；
BIT4
| BIT5 | EOD alarm | ＝0 normal，＝1 alarm
| BIT6 | Parameter setting request flags | =0 The configuration is complete；=1 The configuration is not complete；
| BIT7 | Bus status | =0 normal；=1 Undervoltage；=2 Overvoltage；
BIT8
BIT9
| BIT10 | AC side voltage status | =0 normal；=1abnormal；
| BIT11 | AC side frequence status | =0 normal；=1abnormal；
| BIT12 | AC side phase sequence state | =0 normal；=1abnormal；
| BIT13 | Low power operating state | 1：run；0：Non-running
| BIT14 | Reserved | Reserved
| BIT15 | Whether the module is the primary or not | ＝0 Sub-modules，＝1Main module
u16Word2All | bit0: BIT0; bit1: Boot allowed status; bit2: ＝0 Not allowed，＝1 allow
| BIT1 | Inverter status | ＝0 off，＝1 on
| BIT2 | Power supply status on the inverter side | ＝0 None of them are powered，＝1 Grid power supply，＝2 Inverter power supply，＝3 Output Prohibition (Removal)
BIT3
| BIT4 | Emergency shutdown prompt | ＝0 No，＝1 Yes
| BIT5 | DC side current impulse backfill | ＝0 No，＝2 Yes
BIT6
| BIT7 | Reserved | Reserved
| BIT8 | Reserved | Reserved
| BIT9 | Reserved | Reserved
| BIT10 | Reserved | Reserved
| BIT11 | Reserved | Reserved
| BIT12 | Reserved | Reserved
| BIT13 | Reserved | Reserved
| BIT14 | The power on and off status of the module | ＝0 Off，＝1 On
| BIT15 | Module online flag | ＝0 Not online，＝1 Work online
u16Word3All | bit0: BIT0; bit1: Working state; bit2: 1：Normal off 2：Fault off 3：Normal operation 4：Alarm operation 5：Starting
BIT1
BIT2
| BIT3 | Fault self-locking | 1 Effective
| BIT4 | Remote local | 1：Local:2：Remote
BIT5
| BIT6 | Environmental overtemperature derating | 1 Effective
| BIT7 | Battery-side current limiting derating | 1 Effective
| BIT8 | Current limiting and derating on the grid side | 1 Effective
| BIT9 | Grid overvoltage power derating | 1 Effective
| BIT10 | Grid undervoltage power derating | 1 Effective
| BIT11 | Hot standby operation | Reserved
| BIT12 | Reserved | Reserved
| BIT13 | Reserved | Reserved
| BIT14 | Reserved | Reserved
| BIT15 | Reserved | Reserved
Table3：detailed list of alarm information
Data words | bit0: bit; bit1: state name; bit2: meaning
u16Word1All | bit0: BIT0; bit1: The inverter is out of sync; bit2: ＝0 normal，＝1 Out of sync
| BIT1 | Inverter failure | ＝0 normal，＝1 fault
| BIT2 | The inverter is overheated | ＝0 normal，＝1 overtemperature
| BIT3 | The output is overloaded | ＝0 normal，＝1 overload
| BIT4 | Output overload timeout | ＝0 normal，＝1 timeout
| BIT5 | The working mode is inconsistent | ＝0 normal，＝1 abnormal
| BIT6 | The output voltage is abnormal | ＝0 normal，＝1 abnormal
| BIT7 | Auxiliary power failure | Reserved
| BIT8 | The parameters of the cabinet merging are abnormal | ＝0 normal，＝1 abnormal
| BIT9 | Bus voltage overvoltage shutdown | ＝0 normal，＝1 Abnormal shutdown
| BIT10 | Bus voltage undervoltage shutdown | ＝0 normal，＝1 Abnormal shutdown
| BIT11 | The discrete bus communication in the inverter rack is abnormal | ＝0 normal，＝1 abnormal
| BIT12 | The inverter fan is abnormal | ＝0 normal，＝1 abnormal
| BIT13 | Inverter relay failure | ＝0 normal，＝1 fault
| BIT14 | The output fuse is broken | ＝0 normal，＝1 break
| BIT15 | The parallel interface is abnormal | ＝0 normal，＝1 Abnormal shutdown
u16Word2All | bit0: BIT0; bit1: User action error; bit2: ＝0 normal，＝1 wrong
| BIT1 | The AC amplitude frequency is overrun | ＝0 no，＝1 yes
| BIT2 | Smart toggle power on | ＝0 no，＝1 yes
| BIT3 | The inverter DSP program is incorrect | ＝0 normal，＝1 wrong
| BIT4 | The inverter FPGA program is incorrect | ＝0 normal，＝1 wrong
| BIT5 | EOD | ＝0 normal，＝1EOD
| BIT6 | Smart hand-off shutdown | ＝0 no，＝1 yes
| BIT7 | The external environment is abnormally shut down | ＝0 normal，＝1 abnormal
| BIT8 | Carrier synchronization is abnormal | ＝0 normal，＝1 abnormal
| BIT9 | The power module is not ready | ＝0 normal，＝1 Not ready
| BIT10 | Discrete nodes within the rack are isolated | ＝0 normal，＝1 abnormal
| BIT11 | The in-rack current sharing node is isolated | ＝0 normal，＝1 abnormal
| BIT12 | The power frequency synchronization is abnormal | ＝0 normal，＝1 abnormal
| BIT13 | The pre-charge is abnormally shut down | ＝0 no，＝1 yes
| BIT14 | The AC side shuts down abnormally | ＝0 no，＝1 yes
| BIT15 | The DC side shuts down abnormally | ＝0 no，＝1 yes
u16Word3All | bit0: BIT0; bit1: DC side overcurrent shutdown; bit2: ＝0 normal，＝1 Abnormal shutdown
| BIT1 | Reserved | Reserved
| BIT2 | Reserved | Reserved
| BIT3 | Load shock to bypass | ＝0 no，＝1 yes
| BIT4 | Limit on the number of switches | ＝0 no，＝1 yes
| BIT5 | Reserved | Reserved
| BIT6 | Inverter SCR failure | ＝0 no，＝3 fault
BIT7
| BIT8 | The shutdown output is disconnected | ＝0 no，＝1 yes
| BIT9 | Reserved | Reserved
| BIT10 | Parallel current sharing is abnormal | ＝0 normal，＝1 abnormal
| BIT11 | Reserved | Reserved
| BIT12 | Parallel relay failure | ＝0 normal，＝1 fault
| BIT13 | Reserved | Reserved
| BIT14 | The neighbor request is transferred to the bypass | ＝0 no，＝1 yes
| BIT15 | Reserved | Reserved
Table4：BMSalarm
BIT | bit0: ALARM NAME; bit1: BIT; bit2: ALARM NAME
0 | bit0: Cell overvoltage; bit1: 32; bit2: Fire protection
1 | bit0: Cell undervoltage; bit1: 33; bit2: Parallel communication is abnormal
2 | bit0: Charging overtemperature warning; bit1: 34; bit2: Parallel address conflicts
3 | bit0: Charging low temperature warning; bit1: 35
4 | bit0: Discharge over-temperature warning; bit1: 36
5 | bit0: Discharge low temperature warning; bit1: 37
6 | bit0: Discharge overcurrent warning; bit1: 38
7 | bit0: Charging overcurrent warning; bit1: 39
8 | bit0: Total overvoltage warning; bit1: 40
9 | bit0: Total undervoltage warning; bit1: 41
10 | bit0: The circuit breaker is disconnected; bit1: 42
11 | bit0: Equalization charge failed; bit1: 43
12 | bit0: The voltage of the positive battery pack is unbalanced; bit1: 44
13 | bit0: The voltage of the negative battery pack is unbalanced; bit1: 45
14 | bit0: BMU communication is interrupted; bit1: 46
15 | bit0: Single overvoltage protection; bit1: 47
16 | bit0: Unit undervoltage protection level 1; bit1: 48
17 | bit0: Unit undervoltage protection level 2; bit1: 49
18 | bit0: Charging over-temperature protection; bit1: 50
19 | bit0: Charging low temperature protection; bit1: 51
20 | bit0: Discharge over-temperature protection; bit1: 52
21 | bit0: Discharge cryogenic protection; bit1: 53
22 | bit0: Discharge overcurrent protection level 1; bit1: 54
23 | bit0: Discharge overcurrent protection level 2; bit1: 55
24 | bit0: Charge overcurrent protection level 1; bit1: 56
25 | bit0: Charge overcurrent protection level 2; bit1: 57
26 | bit0: Charge overcurrent protection level 3; bit1: 58
27 | bit0: Total overvoltage protection; bit1: 59
28 | bit0: Total undervoltage protection; bit1: 60
29 | bit0: Charging DC contactor malfunction; bit1: 61
30 | bit0: Discharge DC contactor failure; bit1: 62
31 | bit0: EPO shutdown; bit1: 63
Note on C253: Administrator: 删除

## Hold Register(FUN CODE 03¦06)
Address (DEC) | Address (HEX) | Meaning | Date Type | Data accuracy | Remark | Range | PCMZ50 | PCS系列 | 光储系统 | GRES系统 | MPPT模块
1 | 1 | PCS ON/OFF | uint16 |  |  | ON：AA55¦ OFF：BB66 | √ | √ | √ | √ | ×
2 | 2 | Working Mode | uint16 |  |  | 0：Off Grid Mode， 1：PQ Mode， 2：DC voltage regulation Mode | √ | √ | √ | √ | ×
3 | 3 | Active Power | int16 | kW |  | ±The maximum power of the system (the two values are in balance with each other, total active square + total reactive square <= apparent/square of 0.9) Active power, positive value represents discharge, negative value represents charging | √ | √ | √ | √ | ×
4 | 4 | Reactive Power | int16 | kVar |  |  | √ | √ | √ | √ | ×
5 | 5 | AC Nominal Voltage | uint16 | V |  | 380、400 | √ | √ | √ | √ | ×
6 | 6 | AC Nominal Frequency | uint16 | Hz |  | 50、60 | √ | √ | √ | √ | ×
7 | 7 | DC Charge Voltage | uint16 | V | Battery Group 1 | 500~900 | √ | √ | √ | √ | √
8 | 8 | DC Charge Current Limit | uint16 | A |  | 0~2000 | √ | √ | √ | √ | ×
9 | 9 | DC Discharge Current Limit | uint16 | A |  | 0~5000 | √ | √ | √ | √ | √
10 | A | DC Battery EOD Voltage | uint16 | V |  | 420~840 | √ | √ | √ | √ | ×
11 | B | DC Charge Voltage | uint16 | V | Battery Group 2 | 500~900
12 | C | DC Charge Current Limit | uint16 | A |  | 0~2000
13 | D | DC Discharge Current Limit | uint16 | A |  | 0~5000
14 | E | DC Battery EOD Voltage | uint16 | V |  | 420~840
15 | F | DC Charge Voltage | uint16 | V | Battery Group 3 | 500~900
16 | 10 | DC Charge Current Limit | uint16 | A |  | 0~2000
17 | 11 | DC Discharge Current Limit | uint16 | A |  | 0~5000
18 | 12 | DC Battery EOD Voltage | uint16 | V |  | 420~840
19 | 13 | DC Charge Voltage | uint16 | V | Battery Group 4 | 500~900
20 | 14 | DC Charge Current Limit | uint16 | A |  | 0~2000
21 | 15 | DC Discharge Current Limit | uint16 | A |  | 0~5000
22 | 16 | DC Battery EOD Voltage | uint16 | V |  | 420~840
23 | 17 | DC Charge Voltage | uint16 | V | Battery Group 5 | 500~900
24 | 18 | DC Charge Current Limit | uint16 | A |  | 0~2000
25 | 19 | DC Discharge Current Limit | uint16 | A |  | 0~5000
26 | 1A | DC Battery EOD Voltage | uint16 | V |  | 420~840
27 | 1B | DC Charge Voltage | uint16 | V | Battery Group 6 | 500~900
28 | 1C | DC Charge Current Limit | uint16 | A |  | 0~2000
29 | 1D | DC Discharge Current Limit | uint16 | A |  | 0~5000
30 | 1E | DC Battery EOD Voltage | uint16 | V |  | 420~840
31 | 1F | DC Charge Voltage | uint16 | V | Battery Group 7 | 500~900
32 | 20 | DC Charge Current Limit | uint16 | A |  | 0~2000
33 | 21 | DC Discharge Current Limit | uint16 | A |  | 0~5000
34 | 22 | DC Battery EOD Voltage | uint16 | V |  | 420~840
35 | 23 | DC Charge Voltage | uint16 | V | Battery Group 8 | 500~900
36 | 24 | DC Charge Current Limit | uint16 | A |  | 0~2000
37 | 25 | DC Discharge Current Limit | uint16 | A |  | 0~5000
38 | 26 | DC Battery EOD Voltage | uint16 | V |  | 420~840
39 | 27 | DC Charge Voltage | uint16 | V | Battery Group 9 | 500~900
40 | 28 | DC Charge Current Limit | uint16 | A |  | 0~2000
41 | 29 | DC Discharge Current Limit | uint16 | A |  | 0~5000
42 | 2A | DC Battery EOD Voltage | uint16 | V |  | 420~840
43 | 2B | DC Charge Voltage | uint16 | V | Battery Group 10 | 500~900
44 | 2C | DC Charge Current Limit | uint16 | A |  | 0~2000
45 | 2D | DC Discharge Current Limit | uint16 | A |  | 0~5000
46 | 2E | DC Battery EOD Voltage | uint16 | V |  | 420~840 | √ | √ | √ | √ | ×
47 | 2F | Grid input power limit mode | uint16 |  |  | 0：Generate power for self use， 1：peak power limitation 2：PCS mode | × | √ | √ | √ | ×
48 | 30 | Peak power limit value | uint16 | KVA |  |  | × | √ | √ | √ | ×
49 | 31 | Fixed power factor | int16 | 0.001 |  | 800~1000 | × | √ | √ | √ | ×
50 | 32 | Fault Clear | Pulse signal |  |  | 1: reset
51 | 33 | Year | uint16 |  |  | continuous frame
52 | 34 | Moon | uint16
53 | 35 | Day | uint16
54 | 36 | Time | uint16
55 | 37 | Minute | uint16
56 | 38 | Second | uint16
57 | 39 | BATT 1# BMS enable | uint16 |  |  | 0 Disable，1 enable
58 | 3A | BATT 2# BMS enable | uint16 |  |  | 0 Disable，1 enable
59 | 3B | BATT 3# BMS enable | uint16 |  |  | 0 Disable，1 enable
60 | 3C | BATT 4# BMS enable | uint16 |  |  | 0 Disable，1 enable
61 | 3D | BATT 5# BMS enable | uint16 |  |  | 0 Disable，1 enable
62 | 3E | BATT 6# BMS enable | uint16 |  |  | 0 Disable，1 enable
63 | 3F | BATT 7# BMS enable | uint16 |  |  | 0 Disable，1 enable
64 | 40 | BATT 8# BMS enable | uint16 |  |  | 0 Disable，1 enable
65 | 41 | BATT 9# BMS enable | uint16 |  |  | 0 Disable，1 enable
66 | 42 | BATT 10# BMS enable | uint16 |  |  | 0 Disable，1 enable
67 | 43 | Whether there is an external mobile battery | uint16 |  |  | 0 no , 1 yes